## 691-9-U4
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
US Extremely Inverse (U4) (TCC 691-9-U4) | [9 empty] | US Extremely Inverse (U4) (TCC 691-9-U4) | [9 empty] | US Extremely Inverse (U4) (TCC 691-9-U4)
Average Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Average Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Average Tripping Time-Current Characteristic Curves Dated February 16, 2009
Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of
| current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5
| cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between
| 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting.
| Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup
| current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds.
Time Dial = 0.5 |  | Time Dial = 1.0 |  | Time Dial = 2.0 |  | Time Dial = 3.0 |  | Time Dial = 4.0 |  | Time Dial = 5.0 |  | Time Dial = 6.0 |  | Time Dial = 8.0 |  | Time Dial = 10.0 |  | Time Dial = 12.0 |  | Time Dial = 15.0
*of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s)
1.5 | 2.2856 | 1.5 | 4.5712 | 1.5 | 9.1424 | 1.5 | 13.7136 | 1.5 | 18.2848 | 1.5 | 22.856 | 1.5 | 27.4272 | 1.5 | 36.5696 | 1.5 | 45.712 | 1.5 | 54.8544 | 1.5 | 68.568
1.6 | 1.8349 | 1.6 | 3.6698 | 1.6 | 7.3396 | 1.6 | 11.0094 | 1.6 | 14.6793 | 1.6 | 18.3491 | 1.6 | 22.0189 | 1.6 | 29.3585 | 1.6 | 36.6982 | 1.6 | 44.0378 | 1.6 | 55.0472
1.7 | 1.5176 | 1.7 | 3.0352 | 1.7 | 6.0704 | 1.7 | 9.1056 | 1.7 | 12.1408 | 1.7 | 15.176 | 1.7 | 18.2112 | 1.7 | 24.2816 | 1.7 | 30.352 | 1.7 | 36.4224 | 1.7 | 45.528
1.8 | 1.2832 | 1.8 | 2.5665 | 1.8 | 5.1329 | 1.8 | 7.6993 | 1.8 | 10.2658 | 1.8 | 12.8323 | 1.8 | 15.3987 | 1.8 | 20.5316 | 1.8 | 25.6645 | 1.8 | 30.7974 | 1.8 | 38.4967
1.9 | 1.1038 | 1.9 | 2.2076 | 1.9 | 4.4152 | 1.9 | 6.6228 | 1.9 | 8.8305 | 1.9 | 11.0381 | 1.9 | 13.2457 | 1.9 | 17.6609 | 1.9 | 22.0761 | 1.9 | 26.4914 | 1.9 | 33.1142
2 | 0.9626 | 2 | 1.9252 | 2 | 3.8504 | 2 | 5.7756 | 2 | 7.7008 | 2 | 9.626 | 2 | 11.5512 | 2 | 15.4016 | 2 | 19.252 | 2 | 23.1024 | 2 | 28.878
2.1 | 0.84898 | 2.1 | 1.698 | 2.1 | 3.3959 | 2.1 | 5.0939 | 2.1 | 6.7918 | 2.1 | 8.4898 | 2.1 | 10.1877 | 2.1 | 13.5837 | 2.1 | 16.9796 | 2.1 | 20.3755 | 2.1 | 25.4693
2.2 | 0.75588 | 2.2 | 1.5118 | 2.2 | 3.0235 | 2.2 | 4.5353 | 2.2 | 6.047 | 2.2 | 7.5588 | 2.2 | 9.0706 | 2.2 | 12.0941 | 2.2 | 15.1176 | 2.2 | 18.1411 | 2.2 | 22.6764
2.3 | 0.67844 | 2.3 | 1.3569 | 2.3 | 2.7138 | 2.3 | 4.0706 | 2.3 | 5.4275 | 2.3 | 6.7844 | 2.3 | 8.1413 | 2.3 | 10.855 | 2.3 | 13.5688 | 2.3 | 16.2825 | 2.3 | 20.3532
2.4 | 0.61319 | 2.4 | 1.2264 | 2.4 | 2.4528 | 2.4 | 3.6791 | 2.4 | 4.9055 | 2.4 | 6.1319 | 2.4 | 7.3583 | 2.4 | 9.811 | 2.4 | 12.2638 | 2.4 | 14.7165 | 2.4 | 18.3956
2.5 | 0.5576 | 2.5 | 1.1152 | 2.5 | 2.2304 | 2.5 | 3.3456 | 2.5 | 4.4608 | 2.5 | 5.576 | 2.5 | 6.6912 | 2.5 | 8.9216 | 2.5 | 11.152 | 2.5 | 13.3824 | 2.5 | 16.728
2.6 | 0.50979 | 2.6 | 1.0196 | 2.6 | 2.0391 | 2.6 | 3.0587 | 2.6 | 4.0783 | 2.6 | 5.0979 | 2.6 | 6.1174 | 2.6 | 8.1566 | 2.6 | 10.1958 | 2.6 | 12.2349 | 2.6 | 15.2936
2.7 | 0.46832 | 2.7 | 0.93663 | 2.7 | 1.8733 | 2.7 | 2.8099 | 2.7 | 3.7465 | 2.7 | 4.6832 | 2.7 | 5.6198 | 2.7 | 7.493 | 2.7 | 9.3663 | 2.7 | 11.2396 | 2.7 | 14.0495
2.8 | 0.43207 | 2.8 | 0.86415 | 2.8 | 1.7283 | 2.8 | 2.5924 | 2.8 | 3.4566 | 2.8 | 4.3207 | 2.8 | 5.1849 | 2.8 | 6.9132 | 2.8 | 8.6415 | 2.8 | 10.3698 | 2.8 | 12.9622
2.9 | 0.40019 | 2.9 | 0.80038 | 2.9 | 1.6008 | 2.9 | 2.4011 | 2.9 | 3.2015 | 2.9 | 4.0019 | 2.9 | 4.8023 | 2.9 | 6.4031 | 2.9 | 8.0038 | 2.9 | 9.6046 | 2.9 | 12.0057
3 | 0.37198 | 3 | 0.74395 | 3 | 1.4879 | 3 | 2.2319 | 3 | 2.9758 | 3 | 3.7197 | 3 | 4.4637 | 3 | 5.9516 | 3 | 7.4395 | 3 | 8.9274 | 3 | 11.1593
3.1 | 0.34687 | 3.1 | 0.69374 | 3.1 | 1.3875 | 3.1 | 2.0812 | 3.1 | 2.7749 | 3.1 | 3.4687 | 3.1 | 4.1624 | 3.1 | 5.5499 | 3.1 | 6.9374 | 3.1 | 8.3248 | 3.1 | 10.406
3.2 | 0.32442 | 3.2 | 0.64884 | 3.2 | 1.2977 | 3.2 | 1.9465 | 3.2 | 2.5953 | 3.2 | 3.2442 | 3.2 | 3.893 | 3.2 | 5.1907 | 3.2 | 6.4884 | 3.2 | 7.786 | 3.2 | 9.7325
3.3 | 0.30425 | 3.3 | 0.60851 | 3.3 | 1.217 | 3.3 | 1.8255 | 3.3 | 2.434 | 3.3 | 3.0425 | 3.3 | 3.651 | 3.3 | 4.8681 | 3.3 | 6.0851 | 3.3 | 7.3021 | 3.3 | 9.1276
3.4 | 0.28607 | 3.4 | 0.57213 | 3.4 | 1.1443 | 3.4 | 1.7164 | 3.4 | 2.2885 | 3.4 | 2.8607 | 3.4 | 3.4328 | 3.4 | 4.5771 | 3.4 | 5.7213 | 3.4 | 6.8656 | 3.4 | 8.582
3.5 | 0.2696 | 3.5 | 0.5392 | 3.5 | 1.0784 | 3.5 | 1.6176 | 3.5 | 2.1568 | 3.5 | 2.696 | 3.5 | 3.2352 | 3.5 | 4.3136 | 3.5 | 5.392 | 3.5 | 6.4704 | 3.5 | 8.088
3.6 | 0.25464 | 3.6 | 0.50928 | 3.6 | 1.0186 | 3.6 | 1.5278 | 3.6 | 2.0371 | 3.6 | 2.5464 | 3.6 | 3.0557 | 3.6 | 4.0742 | 3.6 | 5.0928 | 3.6 | 6.1114 | 3.6 | 7.6392
3.7 | 0.241 | 3.7 | 0.48201 | 3.7 | 0.96402 | 3.7 | 1.446 | 3.7 | 1.928 | 3.7 | 2.41 | 3.7 | 2.8921 | 3.7 | 3.8561 | 3.7 | 4.8201 | 3.7 | 5.7841 | 3.7 | 7.2301
3.8 | 0.22854 | 3.8 | 0.45708 | 3.8 | 0.91415 | 3.8 | 1.3712 | 3.8 | 1.8283 | 3.8 | 2.2854 | 3.8 | 2.7424 | 3.8 | 3.6566 | 3.8 | 4.5708 | 3.8 | 5.4849 | 3.8 | 6.8561
3.9 | 0.21711 | 3.9 | 0.43421 | 3.9 | 0.86843 | 3.9 | 1.3026 | 3.9 | 1.7369 | 3.9 | 2.1711 | 3.9 | 2.6053 | 3.9 | 3.4737 | 3.9 | 4.3421 | 3.9 | 5.2106 | 3.9 | 6.5132
4 | 0.2066 | 4 | 0.4132 | 4 | 0.8264 | 4 | 1.2396 | 4 | 1.6528 | 4 | 2.066 | 4 | 2.4792 | 4 | 3.3056 | 4 | 4.132 | 4 | 4.9584 | 4 | 6.198
4.1 | 0.19692 | 4.1 | 0.39383 | 4.1 | 0.78767 | 4.1 | 1.1815 | 4.1 | 1.5753 | 4.1 | 1.9692 | 4.1 | 2.363 | 4.1 | 3.1507 | 4.1 | 3.9383 | 4.1 | 4.726 | 4.1 | 5.9075
4.2 | 0.18797 | 4.2 | 0.37595 | 4.2 | 0.75189 | 4.2 | 1.1278 | 4.2 | 1.5038 | 4.2 | 1.8797 | 4.2 | 2.2557 | 4.2 | 3.0076 | 4.2 | 3.7595 | 4.2 | 4.5113 | 4.2 | 5.6392
4.3 | 0.17969 | 4.3 | 0.35939 | 4.3 | 0.71877 | 4.3 | 1.0782 | 4.3 | 1.4375 | 4.3 | 1.7969 | 4.3 | 2.1563 | 4.3 | 2.8751 | 4.3 | 3.5939 | 4.3 | 4.3126 | 4.3 | 5.3908
4.4 | 0.17201 | 4.4 | 0.34402 | 4.4 | 0.68805 | 4.4 | 1.0321 | 4.4 | 1.3761 | 4.4 | 1.7201 | 4.4 | 2.0641 | 4.4 | 2.7522 | 4.4 | 3.4402 | 4.4 | 4.1283 | 4.4 | 5.1604
4.5 | 0.16487 | 4.5 | 0.32975 | 4.5 | 0.65949 | 4.5 | 0.98924 | 4.5 | 1.319 | 4.5 | 1.6487 | 4.5 | 1.9785 | 4.5 | 2.638 | 4.5 | 3.2975 | 4.5 | 3.9569 | 4.5 | 4.9462
4.6 | 0.15823 | 4.6 | 0.31645 | 4.6 | 0.6329 | 4.6 | 0.94935 | 4.6 | 1.2658 | 4.6 | 1.5822 | 4.6 | 1.8987 | 4.6 | 2.5316 | 4.6 | 3.1645 | 4.6 | 3.7974 | 4.6 | 4.7467
4.7 | 0.15202 | 4.7 | 0.30405 | 4.7 | 0.6081 | 4.7 | 0.91214 | 4.7 | 1.2162 | 4.7 | 1.5202 | 4.7 | 1.8243 | 4.7 | 2.4324 | 4.7 | 3.0405 | 4.7 | 3.6486 | 4.7 | 4.5607
4.8 | 0.14623 | 4.8 | 0.29246 | 4.8 | 0.58492 | 4.8 | 0.87738 | 4.8 | 1.1698 | 4.8 | 1.4623 | 4.8 | 1.7548 | 4.8 | 2.3397 | 4.8 | 2.9246 | 4.8 | 3.5095 | 4.8 | 4.3869
4.9 | 0.14081 | 4.9 | 0.28161 | 4.9 | 0.56323 | 4.9 | 0.84484 | 4.9 | 1.1265 | 4.9 | 1.4081 | 4.9 | 1.6897 | 4.9 | 2.2529 | 4.9 | 2.8161 | 4.9 | 3.3794 | 4.9 | 4.2242
5 | 0.13573 | 5 | 0.27145 | 5 | 0.5429 | 5 | 0.81435 | 5 | 1.0858 | 5 | 1.3573 | 5 | 1.6287 | 5 | 2.1716 | 5 | 2.7145 | 5 | 3.2574 | 5 | 4.0717
5.1 | 0.13095 | 5.1 | 0.26191 | 5.1 | 0.52382 | 5.1 | 0.78573 | 5.1 | 1.0476 | 5.1 | 1.3095 | 5.1 | 1.5715 | 5.1 | 2.0953 | 5.1 | 2.6191 | 5.1 | 3.1429 | 5.1 | 3.9286
5.2 | 0.12647 | 5.2 | 0.25294 | 5.2 | 0.50588 | 5.2 | 0.75883 | 5.2 | 1.0118 | 5.2 | 1.2647 | 5.2 | 1.5177 | 5.2 | 2.0235 | 5.2 | 2.5294 | 5.2 | 3.0353 | 5.2 | 3.7941
5.3 | 0.12225 | 5.3 | 0.2445 | 5.3 | 0.489 | 5.3 | 0.73351 | 5.3 | 0.97801 | 5.3 | 1.2225 | 5.3 | 1.467 | 5.3 | 1.956 | 5.3 | 2.445 | 5.3 | 2.934 | 5.3 | 3.6675
5.4 | 0.11827 | 5.4 | 0.23655 | 5.4 | 0.4731 | 5.4 | 0.70965 | 5.4 | 0.9462 | 5.4 | 1.1827 | 5.4 | 1.4193 | 5.4 | 1.8924 | 5.4 | 2.3655 | 5.4 | 2.8386 | 5.4 | 3.5482
5.5 | 0.11452 | 5.5 | 0.22905 | 5.5 | 0.45809 | 5.5 | 0.68714 | 5.5 | 0.91618 | 5.5 | 1.1452 | 5.5 | 1.3743 | 5.5 | 1.8324 | 5.5 | 2.2905 | 5.5 | 2.7486 | 5.5 | 3.4357
5.6 | 0.11098 | 5.6 | 0.22196 | 5.6 | 0.44392 | 5.6 | 0.66588 | 5.6 | 0.88784 | 5.6 | 1.1098 | 5.6 | 1.3318 | 5.6 | 1.7757 | 5.6 | 2.2196 | 5.6 | 2.6635 | 5.6 | 3.3294
5.7 | 0.10763 | 5.7 | 0.21526 | 5.7 | 0.43051 | 5.7 | 0.64577 | 5.7 | 0.86103 | 5.7 | 1.0763 | 5.7 | 1.2915 | 5.7 | 1.7221 | 5.7 | 2.1526 | 5.7 | 2.5831 | 5.7 | 3.2289
5.8 | 0.10446 | 5.8 | 0.20891 | 5.8 | 0.41783 | 5.8 | 0.62674 | 5.8 | 0.83565 | 5.8 | 1.0446 | 5.8 | 1.2535 | 5.8 | 1.6713 | 5.8 | 2.0891 | 5.8 | 2.507 | 5.8 | 3.1337
5.9 | 0.10145 | 5.9 | 0.2029 | 5.9 | 0.4058 | 5.9 | 0.60871 | 5.9 | 0.81161 | 5.9 | 1.0145 | 5.9 | 1.2174 | 5.9 | 1.6232 | 5.9 | 2.029 | 5.9 | 2.4348 | 5.9 | 3.0435
6 | 0.0986 | 6 | 0.1972 | 6 | 0.3944 | 6 | 0.5916 | 6 | 0.7888 | 6 | 0.986 | 6 | 1.1832 | 6 | 1.5776 | 6 | 1.972 | 6 | 2.3664 | 6 | 2.958
6.1 | 0.095893 | 6.1 | 0.19179 | 6.1 | 0.38357 | 6.1 | 0.57536 | 6.1 | 0.76715 | 6.1 | 0.95893 | 6.1 | 1.1507 | 6.1 | 1.5343 | 6.1 | 1.9179 | 6.1 | 2.3014 | 6.1 | 2.8768
6.2 | 0.093321 | 6.2 | 0.18664 | 6.2 | 0.37328 | 6.2 | 0.55993 | 6.2 | 0.74657 | 6.2 | 0.93321 | 6.2 | 1.1199 | 6.2 | 1.4931 | 6.2 | 1.8664 | 6.2 | 2.2397 | 6.2 | 2.7996
6.3 | 0.090875 | 6.3 | 0.18175 | 6.3 | 0.3635 | 6.3 | 0.54525 | 6.3 | 0.727 | 6.3 | 0.90875 | 6.3 | 1.0905 | 6.3 | 1.454 | 6.3 | 1.8175 | 6.3 | 2.181 | 6.3 | 2.7262
6.4 | 0.088546 | 6.4 | 0.17709 | 6.4 | 0.35418 | 6.4 | 0.53128 | 6.4 | 0.70837 | 6.4 | 0.88546 | 6.4 | 1.0626 | 6.4 | 1.4167 | 6.4 | 1.7709 | 6.4 | 2.1251 | 6.4 | 2.6564
6.5 | 0.086327 | 6.5 | 0.17265 | 6.5 | 0.34531 | 6.5 | 0.51796 | 6.5 | 0.69062 | 6.5 | 0.86327 | 6.5 | 1.0359 | 6.5 | 1.3812 | 6.5 | 1.7265 | 6.5 | 2.0719 | 6.5 | 2.5898
6.6 | 0.084212 | 6.6 | 0.16842 | 6.6 | 0.33685 | 6.6 | 0.50527 | 6.6 | 0.67369 | 6.6 | 0.84212 | 6.6 | 1.0105 | 6.6 | 1.3474 | 6.6 | 1.6842 | 6.6 | 2.0211 | 6.6 | 2.5264
6.7 | 0.082193 | 6.7 | 0.16439 | 6.7 | 0.32877 | 6.7 | 0.49316 | 6.7 | 0.65755 | 6.7 | 0.82193 | 6.7 | 0.98632 | 6.7 | 1.3151 | 6.7 | 1.6439 | 6.7 | 1.9726 | 6.7 | 2.4658
6.8 | 0.080266 | 6.8 | 0.16053 | 6.8 | 0.32106 | 6.8 | 0.48159 | 6.8 | 0.64213 | 6.8 | 0.80266 | 6.8 | 0.96319 | 6.8 | 1.2843 | 6.8 | 1.6053 | 6.8 | 1.9264 | 6.8 | 2.408
6.9 | 0.078424 | 6.9 | 0.15685 | 6.9 | 0.3137 | 6.9 | 0.47054 | 6.9 | 0.62739 | 6.9 | 0.78424 | 6.9 | 0.94109 | 6.9 | 1.2548 | 6.9 | 1.5685 | 6.9 | 1.8822 | 6.9 | 2.3527
7 | 0.076662 | 7 | 0.15332 | 7 | 0.30665 | 7 | 0.45998 | 7 | 0.6133 | 7 | 0.76663 | 7 | 0.91995 | 7 | 1.2266 | 7 | 1.5333 | 7 | 1.8399 | 7 | 2.2999
7.1 | 0.074977 | 7.1 | 0.14995 | 7.1 | 0.29991 | 7.1 | 0.44986 | 7.1 | 0.59982 | 7.1 | 0.74977 | 7.1 | 0.89972 | 7.1 | 1.1996 | 7.1 | 1.4995 | 7.1 | 1.7994 | 7.1 | 2.2493
7.2 | 0.073363 | 7.2 | 0.14673 | 7.2 | 0.29345 | 7.2 | 0.44018 | 7.2 | 0.58691 | 7.2 | 0.73363 | 7.2 | 0.88036 | 7.2 | 1.1738 | 7.2 | 1.4673 | 7.2 | 1.7607 | 7.2 | 2.2009
7.3 | 0.071817 | 7.3 | 0.14363 | 7.3 | 0.28727 | 7.3 | 0.4309 | 7.3 | 0.57453 | 7.3 | 0.71817 | 7.3 | 0.8618 | 7.3 | 1.1491 | 7.3 | 1.4363 | 7.3 | 1.7236 | 7.3 | 2.1545
7.4 | 0.070334 | 7.4 | 0.14067 | 7.4 | 0.28134 | 7.4 | 0.42201 | 7.4 | 0.56268 | 7.4 | 0.70334 | 7.4 | 0.84401 | 7.4 | 1.1254 | 7.4 | 1.4067 | 7.4 | 1.688 | 7.4 | 2.11
7.5 | 0.068912 | 7.5 | 0.13782 | 7.5 | 0.27565 | 7.5 | 0.41347 | 7.5 | 0.5513 | 7.5 | 0.68912 | 7.5 | 0.82695 | 7.5 | 1.1026 | 7.5 | 1.3782 | 7.5 | 1.6539 | 7.5 | 2.0674
7.6 | 0.067547 | 7.6 | 0.13509 | 7.6 | 0.27019 | 7.6 | 0.40528 | 7.6 | 0.54038 | 7.6 | 0.67547 | 7.6 | 0.81057 | 7.6 | 1.0808 | 7.6 | 1.3509 | 7.6 | 1.6211 | 7.6 | 2.0264
7.7 | 0.066236 | 7.7 | 0.13247 | 7.7 | 0.26494 | 7.7 | 0.39742 | 7.7 | 0.52989 | 7.7 | 0.66236 | 7.7 | 0.79483 | 7.7 | 1.0598 | 7.7 | 1.3247 | 7.7 | 1.5897 | 7.7 | 1.9871
7.8 | 0.064976 | 7.8 | 0.12995 | 7.8 | 0.25991 | 7.8 | 0.38986 | 7.8 | 0.51981 | 7.8 | 0.64976 | 7.8 | 0.77972 | 7.8 | 1.0396 | 7.8 | 1.2995 | 7.8 | 1.5594 | 7.8 | 1.9493
7.9 | 0.063765 | 7.9 | 0.12753 | 7.9 | 0.25506 | 7.9 | 0.38259 | 7.9 | 0.51012 | 7.9 | 0.63765 | 7.9 | 0.76518 | 7.9 | 1.0202 | 7.9 | 1.2753 | 7.9 | 1.5304 | 7.9 | 1.913
8 | 0.0626 | 8 | 0.1252 | 8 | 0.2504 | 8 | 0.3756 | 8 | 0.5008 | 8 | 0.626 | 8 | 0.7512 | 8 | 1.0016 | 8 | 1.252 | 8 | 1.5024 | 8 | 1.878
8.1 | 0.061479 | 8.1 | 0.12296 | 8.1 | 0.24591 | 8.1 | 0.36887 | 8.1 | 0.49183 | 8.1 | 0.61479 | 8.1 | 0.73774 | 8.1 | 0.98366 | 8.1 | 1.2296 | 8.1 | 1.4755 | 8.1 | 1.8444
8.2 | 0.060399 | 8.2 | 0.1208 | 8.2 | 0.2416 | 8.2 | 0.36239 | 8.2 | 0.48319 | 8.2 | 0.60399 | 8.2 | 0.72479 | 8.2 | 0.96638 | 8.2 | 1.208 | 8.2 | 1.4496 | 8.2 | 1.812
8.3 | 0.059359 | 8.3 | 0.11872 | 8.3 | 0.23743 | 8.3 | 0.35615 | 8.3 | 0.47487 | 8.3 | 0.59359 | 8.3 | 0.7123 | 8.3 | 0.94974 | 8.3 | 1.1872 | 8.3 | 1.4246 | 8.3 | 1.7808
8.4 | 0.058356 | 8.4 | 0.11671 | 8.4 | 0.23342 | 8.4 | 0.35014 | 8.4 | 0.46685 | 8.4 | 0.58356 | 8.4 | 0.70027 | 8.4 | 0.9337 | 8.4 | 1.1671 | 8.4 | 1.4005 | 8.4 | 1.7507
8.5 | 0.057389 | 8.5 | 0.11478 | 8.5 | 0.22956 | 8.5 | 0.34434 | 8.5 | 0.45912 | 8.5 | 0.57389 | 8.5 | 0.68867 | 8.5 | 0.91823 | 8.5 | 1.1478 | 8.5 | 1.3773 | 8.5 | 1.7217
8.6 | 0.056457 | 8.6 | 0.11291 | 8.6 | 0.22583 | 8.6 | 0.33874 | 8.6 | 0.45166 | 8.6 | 0.56457 | 8.6 | 0.67748 | 8.6 | 0.90331 | 8.6 | 1.1291 | 8.6 | 1.355 | 8.6 | 1.6937
8.7 | 0.055557 | 8.7 | 0.11111 | 8.7 | 0.22223 | 8.7 | 0.33334 | 8.7 | 0.44446 | 8.7 | 0.55557 | 8.7 | 0.66668 | 8.7 | 0.88891 | 8.7 | 1.1111 | 8.7 | 1.3334 | 8.7 | 1.6667
8.8 | 0.054688 | 8.8 | 0.10938 | 8.8 | 0.21875 | 8.8 | 0.32813 | 8.8 | 0.4375 | 8.8 | 0.54688 | 8.8 | 0.65625 | 8.8 | 0.87501 | 8.8 | 1.0938 | 8.8 | 1.3125 | 8.8 | 1.6406
8.9 | 0.053849 | 8.9 | 0.1077 | 8.9 | 0.21539 | 8.9 | 0.32309 | 8.9 | 0.43079 | 8.9 | 0.53849 | 8.9 | 0.64618 | 8.9 | 0.86158 | 8.9 | 1.077 | 8.9 | 1.2924 | 8.9 | 1.6155
9 | 0.053038 | 9 | 0.10608 | 9 | 0.21215 | 9 | 0.31822 | 9 | 0.4243 | 9 | 0.53038 | 9 | 0.63645 | 9 | 0.8486 | 9 | 1.0608 | 9 | 1.2729 | 9 | 1.5911
9.1 | 0.052253 | 9.1 | 0.10451 | 9.1 | 0.20901 | 9.1 | 0.31352 | 9.1 | 0.41803 | 9.1 | 0.52253 | 9.1 | 0.62704 | 9.1 | 0.83606 | 9.1 | 1.0451 | 9.1 | 1.2541 | 9.1 | 1.5676
9.2 | 0.051495 | 9.2 | 0.10299 | 9.2 | 0.20598 | 9.2 | 0.30897 | 9.2 | 0.41196 | 9.2 | 0.51495 | 9.2 | 0.61794 | 9.2 | 0.82392 | 9.2 | 1.0299 | 9.2 | 1.2359 | 9.2 | 1.5449
9.3 | 0.050762 | 9.3 | 0.10152 | 9.3 | 0.20305 | 9.3 | 0.30457 | 9.3 | 0.40609 | 9.3 | 0.50762 | 9.3 | 0.60914 | 9.3 | 0.81219 | 9.3 | 1.0152 | 9.3 | 1.2183 | 9.3 | 1.5229
9.4 | 0.050052 | 9.4 | 0.1001 | 9.4 | 0.20021 | 9.4 | 0.30031 | 9.4 | 0.40042 | 9.4 | 0.50052 | 9.4 | 0.60062 | 9.4 | 0.80083 | 9.4 | 1.001 | 9.4 | 1.2012 | 9.4 | 1.5016
9.5 | 0.049365 | 9.5 | 0.098729 | 9.5 | 0.19746 | 9.5 | 0.29619 | 9.5 | 0.39492 | 9.5 | 0.49365 | 9.5 | 0.59238 | 9.5 | 0.78984 | 9.5 | 0.98729 | 9.5 | 1.1848 | 9.5 | 1.4809
9.6 | 0.048699 | 9.6 | 0.097398 | 9.6 | 0.1948 | 9.6 | 0.29219 | 9.6 | 0.38959 | 9.6 | 0.48699 | 9.6 | 0.58439 | 9.6 | 0.77919 | 9.6 | 0.97398 | 9.6 | 1.1688 | 9.6 | 1.461
9.7 | 0.048054 | 9.7 | 0.096109 | 9.7 | 0.19222 | 9.7 | 0.28833 | 9.7 | 0.38444 | 9.7 | 0.48054 | 9.7 | 0.57665 | 9.7 | 0.76887 | 9.7 | 0.96109 | 9.7 | 1.1533 | 9.7 | 1.4416
9.8 | 0.04743 | 9.8 | 0.094859 | 9.8 | 0.18972 | 9.8 | 0.28458 | 9.8 | 0.37944 | 9.8 | 0.4743 | 9.8 | 0.56915 | 9.8 | 0.75887 | 9.8 | 0.94859 | 9.8 | 1.1383 | 9.8 | 1.4229
9.9 | 0.046824 | 9.9 | 0.093648 | 9.9 | 0.1873 | 9.9 | 0.28094 | 9.9 | 0.37459 | 9.9 | 0.46824 | 9.9 | 0.56189 | 9.9 | 0.74918 | 9.9 | 0.93648 | 9.9 | 1.1238 | 9.9 | 1.4047
10 | 0.046236 | 10 | 0.092473 | 10 | 0.18495 | 10 | 0.27742 | 10 | 0.36989 | 10 | 0.46236 | 10 | 0.55484 | 10 | 0.73978 | 10 | 0.92473 | 10 | 1.1097 | 10 | 1.3871
10.5 | 0.04355 | 10.5 | 0.087099 | 10.5 | 0.1742 | 10.5 | 0.2613 | 10.5 | 0.3484 | 10.5 | 0.4355 | 10.5 | 0.5226 | 10.5 | 0.69679 | 10.5 | 0.87099 | 10.5 | 1.0452 | 10.5 | 1.3065
11 | 0.041225 | 11 | 0.08245 | 11 | 0.1649 | 11 | 0.24735 | 11 | 0.3298 | 11 | 0.41225 | 11 | 0.4947 | 11 | 0.6596 | 11 | 0.8245 | 11 | 0.9894 | 11 | 1.2368
11.5 | 0.0392 | 11.5 | 0.0784 | 11.5 | 0.1568 | 11.5 | 0.2352 | 11.5 | 0.3136 | 11.5 | 0.392 | 11.5 | 0.4704 | 11.5 | 0.6272 | 11.5 | 0.784 | 11.5 | 0.9408 | 11.5 | 1.176
12 | 0.037425 | 12 | 0.07485 | 12 | 0.1497 | 12 | 0.22455 | 12 | 0.2994 | 12 | 0.37425 | 12 | 0.4491 | 12 | 0.5988 | 12 | 0.7485 | 12 | 0.8982 | 12 | 1.1228
12.5 | 0.035861 | 12.5 | 0.071722 | 12.5 | 0.14344 | 12.5 | 0.21517 | 12.5 | 0.28689 | 12.5 | 0.35861 | 12.5 | 0.43033 | 12.5 | 0.57377 | 12.5 | 0.71722 | 12.5 | 0.86066 | 12.5 | 1.0758
13 | 0.034475 | 13 | 0.06895 | 13 | 0.1379 | 13 | 0.20685 | 13 | 0.2758 | 13 | 0.34475 | 13 | 0.4137 | 13 | 0.5516 | 13 | 0.6895 | 13 | 0.8274 | 13 | 1.0342
13.5 | 0.033241 | 13.5 | 0.066483 | 13.5 | 0.13297 | 13.5 | 0.19945 | 13.5 | 0.26593 | 13.5 | 0.33241 | 13.5 | 0.3989 | 13.5 | 0.53186 | 13.5 | 0.66483 | 13.5 | 0.79779 | 13.5 | 0.99724
14 | 0.032138 | 14 | 0.064277 | 14 | 0.12855 | 14 | 0.19283 | 14 | 0.25711 | 14 | 0.32138 | 14 | 0.38566 | 14 | 0.51422 | 14 | 0.64277 | 14 | 0.77132 | 14 | 0.96415
14.5 | 0.031148 | 14.5 | 0.062297 | 14.5 | 0.12459 | 14.5 | 0.18689 | 14.5 | 0.24919 | 14.5 | 0.31148 | 14.5 | 0.37378 | 14.5 | 0.49837 | 14.5 | 0.62297 | 14.5 | 0.74756 | 14.5 | 0.93445
15 | 0.030256 | 15 | 0.060512 | 15 | 0.12102 | 15 | 0.18154 | 15 | 0.24205 | 15 | 0.30256 | 15 | 0.36307 | 15 | 0.4841 | 15 | 0.60513 | 15 | 0.72615 | 15 | 0.90769
16 | 0.028718 | 16 | 0.057435 | 16 | 0.11487 | 16 | 0.17231 | 16 | 0.22974 | 16 | 0.28718 | 16 | 0.34461 | 16 | 0.45948 | 16 | 0.57435 | 16 | 0.68922 | 16 | 0.86153
17 | 0.027444 | 17 | 0.054887 | 17 | 0.10977 | 17 | 0.16466 | 17 | 0.21955 | 17 | 0.27444 | 17 | 0.32932 | 17 | 0.4391 | 17 | 0.54888 | 17 | 0.65865 | 17 | 0.82331
18 | 0.026377 | 18 | 0.052754 | 18 | 0.10551 | 18 | 0.15826 | 18 | 0.21102 | 18 | 0.26377 | 18 | 0.31653 | 18 | 0.42203 | 18 | 0.52754 | 18 | 0.63305 | 18 | 0.79131
19 | 0.025475 | 19 | 0.05095 | 19 | 0.1019 | 19 | 0.15285 | 19 | 0.2038 | 19 | 0.25475 | 19 | 0.3057 | 19 | 0.4076 | 19 | 0.5095 | 19 | 0.6114 | 19 | 0.76425
20 | 0.024705 | 20 | 0.049411 | 20 | 0.098821 | 20 | 0.14823 | 20 | 0.19764 | 20 | 0.24705 | 20 | 0.29646 | 20 | 0.39528 | 20 | 0.49411 | 20 | 0.59293 | 20 | 0.74116
21 | 0.024043 | 21 | 0.048086 | 21 | 0.096173 | 21 | 0.14426 | 21 | 0.19235 | 21 | 0.24043 | 21 | 0.28852 | 21 | 0.38469 | 21 | 0.48086 | 21 | 0.57704 | 21 | 0.7213
22 | 0.02347 | 22 | 0.046939 | 22 | 0.093878 | 22 | 0.14082 | 22 | 0.18776 | 22 | 0.2347 | 22 | 0.28163 | 22 | 0.37551 | 22 | 0.46939 | 22 | 0.56327 | 22 | 0.70409
23 | 0.022969 | 23 | 0.045939 | 23 | 0.091877 | 23 | 0.13782 | 23 | 0.18375 | 23 | 0.22969 | 23 | 0.27563 | 23 | 0.36751 | 23 | 0.45939 | 23 | 0.55126 | 23 | 0.68908
24 | 0.02253 | 24 | 0.045061 | 24 | 0.090122 | 24 | 0.13518 | 24 | 0.18024 | 24 | 0.2253 | 24 | 0.27037 | 24 | 0.36049 | 24 | 0.45061 | 24 | 0.54073 | 24 | 0.67591
25 | 0.022143 | 25 | 0.044287 | 25 | 0.088573 | 25 | 0.13286 | 25 | 0.17715 | 25 | 0.22143 | 25 | 0.26572 | 25 | 0.35429 | 25 | 0.44287 | 25 | 0.53144 | 25 | 0.6643
26 | 0.0218 | 26 | 0.0436 | 26 | 0.0872 | 26 | 0.1308 | 26 | 0.1744 | 26 | 0.218 | 26 | 0.2616 | 26 | 0.3488 | 26 | 0.436 | 26 | 0.5232 | 26 | 0.654
27 | 0.021494 | 27 | 0.042988 | 27 | 0.085977 | 27 | 0.12897 | 27 | 0.17195 | 27 | 0.21494 | 27 | 0.25793 | 27 | 0.34391 | 27 | 0.42988 | 27 | 0.51586 | 27 | 0.64483
28 | 0.021221 | 28 | 0.042441 | 28 | 0.084883 | 28 | 0.12732 | 28 | 0.16977 | 28 | 0.21221 | 28 | 0.25465 | 28 | 0.33953 | 28 | 0.42441 | 28 | 0.5093 | 28 | 0.63662
29 | 0.020975 | 29 | 0.04195 | 29 | 0.0839 | 29 | 0.12585 | 29 | 0.1678 | 29 | 0.20975 | 29 | 0.2517 | 29 | 0.3356 | 29 | 0.4195 | 29 | 0.5034 | 29 | 0.62925
30 | 0.020754 | 30 | 0.041507 | 30 | 0.083014 | 30 | 0.12452 | 30 | 0.16603 | 30 | 0.20754 | 30 | 0.24904 | 30 | 0.33206 | 30 | 0.41507 | 30 | 0.49808 | 30 | 0.62261
31 | 0.020754 | 31 | 0.041507 | 31 | 0.083014 | 31 | 0.12452 | 31 | 0.16603 | 31 | 0.20754 | 31 | 0.24904 | 31 | 0.33206 | 31 | 0.41507 | 31 | 0.49808 | 31 | 0.62261
32 | 0.020754 | 32 | 0.041507 | 32 | 0.083014 | 32 | 0.12452 | 32 | 0.16603 | 32 | 0.20754 | 32 | 0.24904 | 32 | 0.33206 | 32 | 0.41507 | 32 | 0.49808 | 32 | 0.62261
33 | 0.020754 | 33 | 0.041507 | 33 | 0.083014 | 33 | 0.12452 | 33 | 0.16603 | 33 | 0.20754 | 33 | 0.24904 | 33 | 0.33206 | 33 | 0.41507 | 33 | 0.49808 | 33 | 0.62261
34 | 0.020754 | 34 | 0.041507 | 34 | 0.083014 | 34 | 0.12452 | 34 | 0.16603 | 34 | 0.20754 | 34 | 0.24904 | 34 | 0.33206 | 34 | 0.41507 | 34 | 0.49808 | 34 | 0.62261
35 | 0.020754 | 35 | 0.041507 | 35 | 0.083014 | 35 | 0.12452 | 35 | 0.16603 | 35 | 0.20754 | 35 | 0.24904 | 35 | 0.33206 | 35 | 0.41507 | 35 | 0.49808 | 35 | 0.62261
36 | 0.020754 | 36 | 0.041507 | 36 | 0.083014 | 36 | 0.12452 | 36 | 0.16603 | 36 | 0.20754 | 36 | 0.24904 | 36 | 0.33206 | 36 | 0.41507 | 36 | 0.49808 | 36 | 0.62261
37 | 0.020754 | 37 | 0.041507 | 37 | 0.083014 | 37 | 0.12452 | 37 | 0.16603 | 37 | 0.20754 | 37 | 0.24904 | 37 | 0.33206 | 37 | 0.41507 | 37 | 0.49808 | 37 | 0.62261
38 | 0.020754 | 38 | 0.041507 | 38 | 0.083014 | 38 | 0.12452 | 38 | 0.16603 | 38 | 0.20754 | 38 | 0.24904 | 38 | 0.33206 | 38 | 0.41507 | 38 | 0.49808 | 38 | 0.62261
39 | 0.020754 | 39 | 0.041507 | 39 | 0.083014 | 39 | 0.12452 | 39 | 0.16603 | 39 | 0.20754 | 39 | 0.24904 | 39 | 0.33206 | 39 | 0.41507 | 39 | 0.49808 | 39 | 0.62261
40 | 0.020754 | 40 | 0.041507 | 40 | 0.083014 | 40 | 0.12452 | 40 | 0.16603 | 40 | 0.20754 | 40 | 0.24904 | 40 | 0.33206 | 40 | 0.41507 | 40 | 0.49808 | 40 | 0.62261
41 | 0.020754 | 41 | 0.041507 | 41 | 0.083014 | 41 | 0.12452 | 41 | 0.16603 | 41 | 0.20754 | 41 | 0.24904 | 41 | 0.33206 | 41 | 0.41507 | 41 | 0.49808 | 41 | 0.62261
42 | 0.020754 | 42 | 0.041507 | 42 | 0.083014 | 42 | 0.12452 | 42 | 0.16603 | 42 | 0.20754 | 42 | 0.24904 | 42 | 0.33206 | 42 | 0.41507 | 42 | 0.49808 | 42 | 0.62261
43 | 0.020754 | 43 | 0.041507 | 43 | 0.083014 | 43 | 0.12452 | 43 | 0.16603 | 43 | 0.20754 | 43 | 0.24904 | 43 | 0.33206 | 43 | 0.41507 | 43 | 0.49808 | 43 | 0.62261
44 | 0.020754 | 44 | 0.041507 | 44 | 0.083014 | 44 | 0.12452 | 44 | 0.16603 | 44 | 0.20754 | 44 | 0.24904 | 44 | 0.33206 | 44 | 0.41507 | 44 | 0.49808 | 44 | 0.62261
45 | 0.020754 | 45 | 0.041507 | 45 | 0.083014 | 45 | 0.12452 | 45 | 0.16603 | 45 | 0.20754 | 45 | 0.24904 | 45 | 0.33206 | 45 | 0.41507 | 45 | 0.49808 | 45 | 0.62261
46 | 0.020754 | 46 | 0.041507 | 46 | 0.083014 | 46 | 0.12452 | 46 | 0.16603 | 46 | 0.20754 | 46 | 0.24904 | 46 | 0.33206 | 46 | 0.41507 | 46 | 0.49808 | 46 | 0.62261
47 | 0.020754 | 47 | 0.041507 | 47 | 0.083014 | 47 | 0.12452 | 47 | 0.16603 | 47 | 0.20754 | 47 | 0.24904 | 47 | 0.33206 | 47 | 0.41507 | 47 | 0.49808 | 47 | 0.62261
48 | 0.020754 | 48 | 0.041507 | 48 | 0.083014 | 48 | 0.12452 | 48 | 0.16603 | 48 | 0.20754 | 48 | 0.24904 | 48 | 0.33206 | 48 | 0.41507 | 48 | 0.49808 | 48 | 0.62261
49 | 0.020754 | 49 | 0.041507 | 49 | 0.083014 | 49 | 0.12452 | 49 | 0.16603 | 49 | 0.20754 | 49 | 0.24904 | 49 | 0.33206 | 49 | 0.41507 | 49 | 0.49808 | 49 | 0.62261
50 | 0.020754 | 50 | 0.041507 | 50 | 0.083014 | 50 | 0.12452 | 50 | 0.16603 | 50 | 0.20754 | 50 | 0.24904 | 50 | 0.33206 | 50 | 0.41507 | 50 | 0.49808 | 50 | 0.62261
55 | 0.020754 | 55 | 0.041507 | 55 | 0.083014 | 55 | 0.12452 | 55 | 0.16603 | 55 | 0.20754 | 55 | 0.24904 | 55 | 0.33206 | 55 | 0.41507 | 55 | 0.49808 | 55 | 0.62261
60 | 0.020754 | 60 | 0.041507 | 60 | 0.083014 | 60 | 0.12452 | 60 | 0.16603 | 60 | 0.20754 | 60 | 0.24904 | 60 | 0.33206 | 60 | 0.41507 | 60 | 0.49808 | 60 | 0.62261
65 | 0.020754 | 65 | 0.041507 | 65 | 0.083014 | 65 | 0.12452 | 65 | 0.16603 | 65 | 0.20754 | 65 | 0.24904 | 65 | 0.33206 | 65 | 0.41507 | 65 | 0.49808 | 65 | 0.62261
70 | 0.020754 | 70 | 0.041507 | 70 | 0.083014 | 70 | 0.12452 | 70 | 0.16603 | 70 | 0.20754 | 70 | 0.24904 | 70 | 0.33206 | 70 | 0.41507 | 70 | 0.49808 | 70 | 0.62261
75 | 0.020754 | 75 | 0.041507 | 75 | 0.083014 | 75 | 0.12452 | 75 | 0.16603 | 75 | 0.20754 | 75 | 0.24904 | 75 | 0.33206 | 75 | 0.41507 | 75 | 0.49808 | 75 | 0.62261
80 | 0.020754 | 80 | 0.041507 | 80 | 0.083014 | 80 | 0.12452 | 80 | 0.16603 | 80 | 0.20754 | 80 | 0.24904 | 80 | 0.33206 | 80 | 0.41507 | 80 | 0.49808 | 80 | 0.62261
85 | 0.020754 | 85 | 0.041507 | 85 | 0.083014 | 85 | 0.12452 | 85 | 0.16603 | 85 | 0.20754 | 85 | 0.24904 | 85 | 0.33206 | 85 | 0.41507 | 85 | 0.49808 | 85 | 0.62261
90 | 0.020754 | 90 | 0.041507 | 90 | 0.083014 | 90 | 0.12452 | 90 | 0.16603 | 90 | 0.20754 | 90 | 0.24904 | 90 | 0.33206 | 90 | 0.41507 | 90 | 0.49808 | 90 | 0.62261
95 | 0.020754 | 95 | 0.041507 | 95 | 0.083014 | 95 | 0.12452 | 95 | 0.16603 | 95 | 0.20754 | 95 | 0.24904 | 95 | 0.33206 | 95 | 0.41507 | 95 | 0.49808 | 95 | 0.62261
100 | 0.020754 | 100 | 0.041507 | 100 | 0.083014 | 100 | 0.12452 | 100 | 0.16603 | 100 | 0.20754 | 100 | 0.24904 | 100 | 0.33206 | 100 | #DIV/0! | 100 | 0.49808 | 100 | 0.62261